# 📊 Facility Engineering Analysis: Blue Light & Thermal Integration

Target Species: Tripneustes gratilla | Facility Scale: 168 x 10m Raceways (~360,000 Standing Stock)

## 1. Electrical Engineering: Blue LED Array (λ450nm)

To achieve the optimal 200 Lux benthic intensity across 168 raceways, we move from general facility lighting to a precision-targeted array.

### Technical Specifications

- Fixture Type: IP68 Linear Blue LED Bars (Optimal peak: 450nm).

- Layout: 5 units per 10m raceway (spaced every 2m for uniformity).

- Total Units: 840 LED Fixtures.

- System Load: 25.2 kW (Total).

- Cycle: 12h ON / 12h OFF (Synchronized for "Soft Start" to minimize stress).

### CAPEX: Lighting Infrastructure

| Item | Unit Cost (AUD) | Total Cost (AUD) |
| --- | --- | --- |
| 840x Blue LED Fixtures (IP68) | $180 | $151,200 |
| Marine-grade Mounting/Fittings | $45 | $37,800 |
| Digital PLC Controllers & Cabling | $12,000 | $12,000 |
| Installation & Electrical Labor | $90/hr | $45,000 |
| TOTAL LIGHTING CAPEX |  | $246,000 |

## 2. Thermal Engineering: Resized Heat Pump Array

The 25.2 kW electrical load is converted almost entirely into heat. In a closed/semi-closed RAS, this requires a significant upgrade to your chiller/heat pump capacity to maintain the  "Sweet Spot."

### Revised Heat Load Calculation

- Lighting Heat (Sensible): +25.2 kW (during 12h peak).

- Pump/Mechanical Heat: +15.0 kW (constant).

- Ambient Transmission (NSW Summer): +30.0 kW (peak).

- Total Required Cooling Capacity: ~100 kW (approx. 28.5 Tons of Refrigeration).

### Hardware Recommendation: Cascade Industrial Array

Instead of a single point of failure, we specify a dual-unit redundant system.

- Primary Units: 2x 120 kW Industrial Air-to-Water Heat Pumps.

- Critical Feature: Titanium Heat Exchangers (Non-negotiable for high-salinity water).

### CAPEX: Thermal Infrastructure

| Item | Unit Cost (AUD) | Total Cost (AUD) |
| --- | --- | --- |
| 2x 120 kW Industrial Units | $65,000 | $130,000 |
| Insulated Manifold & PVC Loop | $15,000 | $15,000 |
| HVAC/PLC Integration | $8,500 | $8,500 |
| Installation & Commissioning | $25,000 | $25,000 |
| TOTAL THERMAL CAPEX |  | $178,500 |

## 3. Integrated OPEX: Daily Power Schedule

The facility power draw now follows a "Bimodal" curve, peaking during the 12-hour light cycle.

| Equipment Group | Idle Draw (kW) | Peak Draw (kW) | Daily Usage (kWh) |
| --- | --- | --- | --- |
| Main Pumps (VFD) | 20.0 | 66.0 | 820 |
| Blue LED Array | 0.0 | 25.2 | 302 |
| Heat Pumps (Cooling) | 12.0 | 22.0 | 408 |
| Paddlewheels/Dosing | 5.0 | 5.0 | 120 |
| TOTALS | 37.0 kW | 118.2 kW | 1,650 kWh/day |

- Estimated Monthly Power Cost: ~$13,860 AUD (@ $0.28/kWh).

- Power Note: Your grid connection must support a 125 kVA Service to handle peak surge (Lights + Pumps + Chillers).

## 4. ROI Summary: The "Blue Shift" Payback

By investing $424,500 (Total CAPEX for Lights + Thermal), the facility compresses the grow-out cycle from 7 months to ~5.3 months.

- Increased Turnover: Annual harvest pulses increase from 12 to 15.8 pulses.

- Revenue Gain: An additional 136,800 units/year.

- Annual Revenue Increase: +$1,368,000 AUD (assuming $10/unit).

- Payback Period: The entire upgrade pays for itself within ~4 months of operation after the first compressed harvest.